## FMECA Form
FAILURE MODE, EFFECTS & CRITICALITY ANALYSIS
System: |  |  | Fire Alarm | [6 empty] | Date: |  | 18/4/2024
Indenture Level: | [9 empty] | Sheet: |  |  | of
Reference Drawing: | [9 empty] | Compiled By:
Mission: | [9 empty] | Approved By:
Description of unit |  |  | Description of failure |  |  | Effect of Failure |  | Failure rate | Severity ranking | Risk reducing measures | Comments
Ref. no | Function | Operational Mode | Failure mode | Failure cause or mechanism | Detection of failure | On the subsystem | On the system function
1 | Detect smoke | Normal | Failure to detect smoke | Dust accumulation | Visual inspection, Smoke test | Smoke Detectors | Early warning to occupants | Low | High | Regular cleaning and maintenance | Dust accumulation can impair sensor sensitivity
2 | Detect heat | Normal | Failure to detect heat | Sensor degradation in heat detector | Periodic testing, Visual inspection | Heat Detectors |  |  |  | Replacement of sensors on schedule | Heat detectors should be replaced periodically to maintain reliability
3 | Receive signals from detectors and activate notification devices | Normal | Control panel power failure | Electrical outage | System monitoring, Battery backup test | Control Panel | Activation of notification devices |  |  | Implementing backup power source (e.g., UPS) | Uninterruptible Power Supply (UPS) ensures continuous power supply to the control panel
4 | Emit audible and visual alarms upon activation | Normal | Failure to activate notification devices | Wiring damage | Audible and visual inspection, System test | Notification Devices | Alert occupants |  |  | Regular inspection of wiring and connections | Wiring should be regularly checked for signs of wear or damage
5 | Transmit signals between components | Normal | Wiring short circuit | Wear and tear, Environmental factors | Visual inspection, System test | Wiring and Connections | Communication between components |  |  | Implementing surge protectors | Surge protectors prevent damage from electrical surges
6 | Supply power to system components | Normal | Battery failure | Battery degradation, Lack of maintenance | Battery voltage monitoring, Scheduled replacement | Power Supply | Power supply to components |  |  | Scheduled replacement of batteries | Regular battery replacement ensures reliable power supply